## Pump Selection (Main Sheet)
Indipendent Variables | [5 empty] | Pump Selection | Dependent Variables |  |  |  |  | Rho*g = | 5346.45 | [6 empty] | Velocity | Suction side | 0.0050375 | [5 empty] | From Working Guide to Pumps and Pumping Stations by Menon (2010)
Variable | SI Value | SI Unit | Unit /Type | Value | ~ L (M) |  | Variable | SI Value | SI Unit | Kg/cm2 | ft | Units | [7 empty] | Head | Deliveryside | 0.025502 |  |  | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59
Desired Flow | 0.0055556 | M3/Sec | KL/Hr | 20 |  |  | NPSH - Available | 60.0097 | M |  |  | Flow | M3/s | KL/Hr | LPM | LPS | [7 empty] | K Factors | 0.015 | 0.02 | 0.025 | 0.032 | 0.04 | 0.05 | 0.065 | 0.08 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6
Desity | 545 | M3/Kg | Sp Gravity | 0.545 |  |  | Velosity in suction side | 0.31438 | M/s |  |  | Desity | Kg/M3 | Sp Gravity | Kg/L | [7 empty] | 4 | 90 Elbow | 0.81 | 0.75 | 0.69 | 0.75 | 0.63 | 0.57 | 0.54 | 0.54 | 0.51 | 0.45 | 0.42 | 0.42 | 0.39 | 0.39 | 0.39 | 0.36 | 0.36 | 0.36 | 0.36
Dynamic Viscosity | 0.000218 | N-s/m2 | cSt | 0.4 |  |  | Velocity in delivery side | 0.70736 | M/s |  |  | D Viscosity | N-s/m2 | Poise | cPoise | M2/s | St | cSt | 4e-07 |  |  |  | 5 | 45 Elbow | 0.43 | 0.4 | 0.37 | 0.35 | 0.34 | 0.3 | 0.29 | 0.29 | 0.27 | 0.24 | 0.22 | 0.22 | 0.21 | 0.21 | 0.21 | 0.19 | 0.19 | 0.19 | 0.19
Kinamatic Viscosity | 4e-07 | M2/s | M2/s |  |  |  | Reynold's Number suction side | 117892.5504 | Unitless |  |  | K Viscosity | M2/s | St | cSt | [7 empty] | 6 | Tee - Thru flow | 0.54 | 0.5 | 0.46 | 0.44 | 0.42 | 0.38 | 0.36 | 0.36 | 0.34 | 0.3 | 0.28 | 0.28 | 0.26 | 0.26 | 0.26 | 0.24 | 0.24 | 0.24 | 0.24
Acceleration due to gravity | 9.81 | M/s2 | M/s2 | 9.81 |  |  | Type of Flow suction side | Turbulent |  |  |  | Acceleration | M/s2 | [9 empty] | 7 | Tee - Thru branch | 1.62 | 1.5 | 1.38 | 1.5 | 1.26 | 1.14 | 1.08 | 1.08 | 1.02 | 0.9 | 0.84 | 0.84 | 0.78 | 0.78 | 0.78 | 0.72 | 0.72 | 0.72 | 0.72
Suction Pipe Diameter | 0.15 | M | mm | 150 |  |  | Darcy's friction factor Suction side | 0.017082 | Unitless |  |  | Length | M | KM | ft | [7 empty] | 8 | Gate Valve | 0.22 | 0.2 | 0.18 | 0.18 | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | 0.12 | 0.11 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Delivery Pipe Diameter | 0.1 | M | mm | 100 |  |  | Reynold's Number Delivery side | 176838.8257 | Unitless |  |  | Units | No | [9 empty] | 9 | Ball Valve | 0.08 | 0.08 | 0.07 | 0.07 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Suction Pipe Length | 50 | M | M | 50 | 50 |  | Type of flow Delivery side | Turbulent |  |  |  | Pressure/Head | M | Pa | Kg/cm2 | <Empty> | ft | Psi |  |  |  |  | 10 | Globe Valve / NRV | 9.2 | 8.5 | 7.8 | 7.5 | 7.1 | 6.5 | 6.1 | 6.1 | 5.8 | 5.1 | 4.8 | 4.8 | 4.4 | 4.4 | 4.4 | 4.1 | 4.1 | 4.1 | 4.1
Suction side number of fittings / Valves -1 | 0 | No | 90 Elbow | 0 | 5 |  | Darcy's friction factor delivery side | 0.01581 | Unitless |  |  | Pipe Side | mm | Inch | cm | m | [6 empty] | 11 | Plug Valve | 0.49 | 0.45 | 0.41 | 0.4 | 0.38 | 0.34 | 0.32 | 0.32 | 0.31 | 0.27 | 0.25 | 0.25 | 0.23 | 0.23 | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
Suction side number of fittings / Valves -2 | 0 | No | 45 Elbow | 0 | 2 |  | Head loss in suction side | 0.036141 | M | 0.0019322 | 0.11857 | Valve Type | Gate Valve | Ball Valve | Globe Valve | Plug Valve | [8 empty] | 0.5 | 0.75 | 1 | 1.25 | 1.5 | 2 | 2.5 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
Suction side number of fittings / Valves -3 | 0 | No | Ball Valve | 0 | 4 |  | Head loss in delivery side | 0.77845 | M | 0.04162 | 2.554 | Bends | 90 Elbow | 45 Elbow | Tee - Thru flow | Tee - Thru branch |  |  |  | Delivery dia | 49
Suction side number of fittings / Valves -4 | 0 | No | Gate Valve | 0 | 0 |  | Head loss at entry & exit | 0.028021 | M | 0.0014981 | 0.091932 | [8 empty] | Suction dia | 50 |  |  | k value | 41: Multiphy Quantity & velocity head
Suction side number of fittings / Valves -5 | 0 | No | Tee - Thru branch | 0 | 2 |  | Velocity head required to maintaine flow | 0.025502 | M | 0.0013635 | 0.083668 | Suction Side friction factor |  |  | by RK Bansal |  |  |  |  | Valve type | 6 |  | S Type1 | 0.45
Suction side number of fittings / Valves -6 | 0 | No | Plug Valve | 0 | 0 |  | Delivery Elevation + Head Required | 298.578 | M | 15.9633 | 979.5866 | Re<2000 | 2000<Re<100000 | Re>100000 | [8 empty] | S Type2 | 0.24
Suction head (available, if any) | 137.6147 | M | Kg/cm2 | 7.5 |  |  | Suction Elevation + Head Available | 142.6147 | M | 7.6248 | 467.8959 | 0.00054287 | 0.017075 | 0.017082 | [8 empty] | S Type3 | 0.05
Suction side elevation (wrt pump's eye) | 5 | M | M | 5 | (-ve if below) |  | Head Required | 156.7953 | M | 8.383 | 514.4202 | Delivery side friction factor | [10 empty] | S Type4 | 0.12
Vapor Pressure at working temperature | 82.5688 | M | Kg/cm2 | 4.5 |  |  | Head Selected | 165 | M | 8.8216 | 541.3386 | Re<2000 | 2000<Re<100000 | Re>100000 | [8 empty] | S Type5 | 0.9
Delivery Pipe Length | 150 | M | M | 150 | 150 |  | Pumping Power Required | 4.9009 | kW | 60% | Brake Eff | 0.00036191 | 0.015429 | 0.01581 | [8 empty] | S Type6 | 0.27
Delivery side number of fittings / Valves -1 | 6 | No | 90 Elbow | 6 | 19.3548 |  | Brake Power | 8.1682 | kW | 85% | Motor Eff | [11 empty] | D Type1 | 0.51
Delivery side number of fittings / Valves -2 | 2 | No | 45 Elbow | 2 | 3.4156 |  | Motor Power | 9.6096 | kW | 12.8867 | HP | [11 empty] | D Type2 | 0.27
Delivery side number of fittings / Valves -3 | 3 | No | Ball Valve | 3 | 0.94876 |  | Monthly Power loss Due to selected Dia | 21623.9992 | kW | 6.0067 | Unit | [11 empty] | D Type3 | 0.05
Delivery side number of fittings / Valves -4 | 3 | No | Tee - Thru branch | 3 | 19.3548 |  | Rs / Month Due to Selected Dia | 72.08 | Rs | 864.96 | Annually | [11 empty] | D Type4 | 1.02
Delivery side number of fittings / Valves -5 | 0 | No | Globe Valve / NRV | 0 | 0 | [17 empty] | D Type5 | 5.8
Delivery side number of fittings / Valves -6 | 0 | No | Plug Valve | 0 | 0 | [17 empty] | D Type6 | 0.31
Discharge head (required) | 293.578 | M | Kg/cm2 | 16
Discharge side elevation (wrt pump's eye) | 5 | M | M | 5
Electricity Board Coversion Rate | 12 | Rs/ Unit | Rs/ Unit | 12 | 200
56.0739
256.0739
Note: 1. Please edit yellow highted shells only. This can be done by providing parametric input or selecting a data from the drop down as applicable.
2. Currency and electricity prices are given using INR currency same can be modified as per the requirement
3. User is required to provide the physical properties of the fluid being pumped & number of valvles / fittings
4. Designer must carefully select the sizes of the suction and delivery pipes to balance between material cost and pumping cost over design life

## Pipe Selection
Media |  |  |  |  | GI coating with IS 4736. | [12 empty] | Media | Water | Air | Gasoline | Diesel | LPG | Ethanol | BioDiesel | Kerosene | Other
Internal Pressure |  | 0.74316 | Mpa |  | welding electrode conforming to IS 814
Design Pressure |  | 2.2295 | Mpa |  | Welding procedure should conform to ASME SEC IX/API 1104 as applicable
Weld Joint Factor | E | 1 |  |  | Read IS 1239-2 for fittings/ forged type manuacturing
Design Factor | F | 0.52 |  |  | Compare spec provided for itme by firecon for each item
Yeild Strength | Y | 205 | Mpa |  | Pipe NPS12 (DN 300) size or smaller have outside diameter numericaly larger than teir corresponding sizes. In contrast, the outside diameter of tubes are identical to thr size number for all sizes.
Maxm Allowable hoop stress | S | 106.6
D/t Ratio |  | 956.2812
External Dia |  | 5000 | [6 empty] | Apart from Hydro static test, flattening test is impportant to check ductility of pipe
Tickness |  | 5.2286 |  |  | Grade/Class | Scope | Ordering information | Designation | Minimum Hydrotest Pressure | Matrial Std | Dimension std | Chemical composition | Marking - Embosing with code | Marking - Color band | Maximum permisible Pressure
Code
1 | For steam/ Water / Air puprpose |  | Size upto 168mm | IS 1239 -1 | Light | This standard ( Part 1 ) covers the requirements for welded and seamless plain end or screwed and socketed steel tubes intended for use for water, non-hazardous gas, air and steam. This standard is applicable to tubes of size 6 mm nominal bore to ISO mm nominal bore. | Refer code for detailed ordering information | Steel tube scovered byt his standard shall be designated by their nominal bore and shall be further classified as light, medium and heavy depending on the wall thickness; and screwed and socketed or plain-end/ bevel-end to denote end condition, and black or galvanized to denote surface condition. Steel tubes shall be manufactured by one ofthe following processes: a) HOI-finishedseamless (HFS); b) Electric resistance welded (ERW); c) High frequency induction welded (HFIW); d) Hot-finished welded (HFW); and e) Cold-finished seamless (CDS) Light, medium and heavy tubes shall be either welded or seamless as agreed to between the purchaser and the manufacturer All electric welded tubes used for steam services shall be normalized. Only medium and heavy class of tube shall normally be used for steam services. For steam service, extra white band to be provided. Where tubes are required to be galvanized, the zinc coating on the tubes shall be in accordance with IS 4736. | 5Mpa minimum for 3 hours with water. It can be done by eddy current method also as described in code. |  |  | 5Mpa minimum for 3 hours with water. It can be done by eddy current method also as described in code. | IS 1239-2 L | Yellow band | for screwed/ socket end pipes refer table A1 in code, for butt welded, flanged coupling pipes Pmax will 2.06Mpa & Tmax will be 260 deg celcius | Minimum 320mpa tensile stregth, thickness varies with class | Choose suitable class by comparing D/t ratio in all classes for give D
[5 empty] | Heavy | [6 empty] | 5Mpa minimum for 3 hours with water. It can be done by eddy current method also as described in code. | IS1239-2 H | Red band |  | Minimum 320mpa tensile stregth, thickness varies with class
[5 empty] | Medium | [6 empty] | 5Mpa minimum for 3 hours with water. It can be done by eddy current method also as described in code. | IS 1239-M | Blue Band |  | Minimum 320mpa tensile stregth, thickness varies with class
2 | For for seavage/ Water / Air puprpose |  | Size more than 168mm | IS 8539 -1 | Fe330 | To standard applies to seamless an dwelded carbon steel pipe for seavage and water carying purpose fro outside dia 168.3mm to 2540mm. | Refer code for detailed ordering information | Pipe designation to be written as method of manufacture then grade number. Method of manufacture - ERW or SAW or S for seamless , size of pipe indicates outer dia, unlike in is1239 where size was written for nominal bore. ERW- Fe410 means ERW manufactured pipe with minimum tensile strength 410Mpa | 5Mpa minimum for 3 hours with water. |  |  | Match from Code for chemical composition / laddle analysis and permissible variation | Manufacturer name -OD - wall thickness - Method of manufacture -maximum tensile stregth. Eg. ABC Company 508.0 8 SAW 410 |  | ?? | Minimum 330mpa tensile stregth, 4 thickness variations are there in ocde for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
[5 empty] | Fe410 | [6 empty] | Match from Code for chemical composition / laddle analysis and permissible variation |  |  |  | Minimum 410mpa tensile stregth, 4 thickness variations are there in ocde for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
[5 empty] | De450 | [6 empty] | Match from Code for chemical composition / laddle analysis and permissible variation |  |  |  | Minimum 450mpa tensile stregth, 4 thickness variations are there in ocde for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
3 | For High temperature /LPG |  | NPS 1⁄8 to NPS 48 | ASTM A106 | A | This speciﬁcation2 covers seamless carbon steel pipe for high-temperature service (Note 1) in NPS 1⁄8 to NPS 48 inclusive, with nominal (average) wall thickness as given in ANSI B 36.10. | Refer code for detailed ordering information |  | Hydrotest as per ASME A 530/A 530M |  |  | Match from Code for grade wise chemical composition / laddle analysis and permissible variation | Marking as per ASME A 530/A 530M |  |  | Minimum 330mpa tensile stregth(210YS), Pipe schedule & thickness variations are there in code ASTM A106 (Cross verify with ASMEB36.10) for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
[5 empty] | B |  |  |  | Hydrotest as per ASME A 530/A 530M |  |  | Match from Code for grade wise chemical composition / laddle analysis and permissible variation | Marking as per ASME A 530/A 530M |  |  | Minimum 415mpa tensile stregth(240YS), Pipe schedule & thickness variations are there in codeASTM A106 (Cross verify with ASMEB36.10) for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
[5 empty] | C |  |  |  | Hydrotest as per ASME A 530/A 530M |  |  | Match from Code for grade wise chemical composition / laddle analysis and permissible variation | Marking as per ASME A 530/A 530M |  |  | Minimum 485mpa tensile stregth(275 YS), Pipe schedule & thickness variations are there in codeASTM A106 (Cross verify with ASMEB36.10) for each OD selected, Choose suitable thickness by comparing D/t ratio in all classes for give D
4 | Metal-Arc-Welded Steel Pipe for Use With HighPressure Transmission Systems |  |  | A 381
5 | Centrifugally Cast Ferritic Alloy Steel Pipe for HighTemperature Service |  |  | A 426
6 | Centrifugally Cast Austenitic Steel Pipe for HighTemperature Service |  |  | A 451
7 | Seamless Carbon Steel Pipe for Atmospheric and Lower Temperatures |  |  | A 524
8 | Centrifugally Cast Iron-Chromium-Nickel High-Alloy Tubing for Pressure Application at High Temperatures |  |  | A 608
9 | Centrifugally Cast Carbon Steel Pipe for HighTemperature Service |  |  | A 660
10 | Electric-Fusion-Welded Steel Pipe for Atmospheric and Lower Temperatures |  |  | A 671
11 | Electric-Fusion-Welded Steel Pipe for High-Pressure Service at Moderate Temperatures |  |  | A 672
3A | Standardization of dimension// Supplymentry |  |  | ASME B.36.10 | Variatou schedule based on D/t ration or thickness. (Refer table 1 of code) | This specification coveres standardization of dimension of welded and seamless wrought steel pipes for hig or low temperature of pressure | [5 empty] | Dimesional stard for pipe described here are covered in respective ASTM codes (for chemical composition/ material strength) |  |  |  | Selection of wall thickness depends primarily upon capacity to resist internal pressure under given condition, this designer shall calculateexact value of wall thickness suitable for ccondition for which pipe is required as prescribed in detail in ASME boiler & pressure code B31 code for pressure piping or other similar code whichever governs the construction thickness shall be selected from table 1 to suit the condition for which the pipe is desired.
3B | Test, tolerance, strength, marking & other detailed specification for al ASTM pipe codes // Supplementary |  |  | ASME A 530/A 530M | Refer code for certified test report requirement to be prodcued by manufacturer, Certiﬁed test report shall include the following information and test results, when applicable: 22.2.1 Heat Number, 22.2.2 Heat Analysis, 22.2.3 Product Analysis, if speciﬁed or required, 22.2.4 Tensile Properties, 22.2.5 Width of the gage length, when longitudinal strip tension test specimens are used, 22.2.6 Bend Test acceptable, 22.2.7 Flattening Test acceptable, 22.2.8 Hydrostatic Test pressure 22.2.9 Non-destructive Electric Test method, 22.2.10 Impact Test results, and 22.2.11 Other test results or information required to be reported by the product speciﬁcation | This speciﬁcation covers a group of requirements which are mandatory requirements to the ASTM pipe product speciﬁcations noted below unless the product speciﬁcation speciﬁes different requirements, in which case the requirement of the product speciﬁcation shall prevail. In case of conﬂict between a requirement of the product speciﬁcation and a requirement of this general requirement speciﬁcation, only the requirement of the product speciﬁcation need be satisﬁed. |  | Rerer code for product marking, designation will be accordance with individual code | 2.1 each length of pipe shall be tested by the manufacturer to a hydrostatic pressure which will produce in the pipe wall a stress not less that 60 % of the minimum speciﬁed yield strength for carbon and ferritic alloy steel pipe, or 50 % of the speciﬁed minimum yield strength for austenitic alloy steel pipe. The test pressure or stress shall be determined by the following equation: P = 2St/D or S= PD/2t . The hydrostatic test pressure determined by the equation shall be rounded to the nearest 50 psi [0.5 MPa] for pressures below 1000 psi [7 MPa], and to the nearest 100 psi [1 MPa] for pressures 1000 psi [7 MPa] and above. The hydrostatic test may be performed prior to cutting to ﬁnal length, or prior to upsetting, swaging, expanding, bending, or other forming operations Regardless of pipe-wall stress-level determined by Eq 3, the minimum hydrostatic test pressure required to satisfy these requirements need not exceed 2500 psi [17.0 MPa] for outside diameters (see D in 21.1) of 3.5 in. [88.9 mm] or less, nor 2800 psi [19.0 MPa] for outside diameters over 3.5 in. [88.9 mm]. This does not prohibit testing at higher pressures at the manufacturer’s option or as provided in 21.3. 21.3 With concurrence of the manufacturer, a minimum hydrostatic test pressure in excess of the requirements of 21.2 or 21.1, or both, may be stated on the order The test pressure shall be held for a minimum of 5 s, without resultant leakage through the pipe wall. For welded pipe, the test pressure shall be held for a time sufficient to permit the inspector to examine the entire length of the welded seam. |  |  | As per respecive specification | Rerer code for product marking, designation will be accordance with individual code |  | See hydrotest pressure section | Minimum tesnile /YS to be as per respective code. Minimum thickness(tolerance) corresponding to pipe thickness selected from any ASTM code is listed in tableX1.1 of code.
4A | Power Piping |  |  | ASME B31.1
4B | Fuel gas piping |  |  | ASME B31.2
4C | Process piping |  |  | ASME B31.3
4D | Pipeline transportation sytem for liquid hydrocarbons and othe liquids // Design procedure for pipes (Parent document of ASTM A series) |  |  | ASME B31.4
4E | Refrigeration piping and heat transfer components |  |  | ASME B31.5
4F | Gas transmission & distributio piing system |  |  | ASME B31.8
4G | Managing system intigrity of gas pipeline |  |  | ASME B31.9
4H | Slurry Transportation piping system |  |  | ASME B31.11
4I | Hydrogen piping & pipelines |  |  | ASME B31.12
4J | Manual for determining remaining strength of corroded pipe |  |  | ASME B31G
12 |  |  |  | API 5L
Pipe fittings
Bend
Tee
Reducer
Flange
Nuts & Bols
Gasket |  |  |  | IS 2712
ANSI B 16.21
Welding Procedure
Welding rod
Weld procedure
Additional requirement
GI coating
Threading
Paintings
Blasting / surface preperation

## Notes
Smooth pipes
| Q | 0.013889 | For Re<2000 | 4000<Re<100000 | Re Beyond 100000 (Approximation) | For rough pipes & commercial pipes formula is RK bansal page 452 to be solved by trial error method, it includes roughness factor k)
| V | 0.78595 |  |  | Actual Eqn for Re beyond 1000000 is in RK Bansal Pg 452(it can be solved by trial error method only) along with other formulas written here.
Pipe length | L | 300
| g | 9.81
Dia of pipe | D | 0.15 | 150
Darcy Weishbathc co-efficeint of friction | f | 0.002 | 2.7392e-05 | 0.0028612 | 0.0031751 | Calculate by trial error also.
Friction factor |  | 0.008
Head loss | h | 0.50375 | Check Chezy's also
Density | Rho | 545 |  |  |  |  | 0.00020183
Kinematic Viscosity | Nu | 2.0183e-07
Dynamic Viscosity | Mu | 0.00011
Characteristic Length | l | 0.15
Reynold's Number | Re | 584103.9999 | We need to decrease pipe size with increasing velosity, to keep Reynold number in laminar range
Type of flow (for pipes) |  | Transit / Turbulent
Calculation of pump head (for design) | Maxm Head required at filling gun+ Maxm static head discharge side+Maxm head loss with rated Q- Min static head suction side - Min vappor pressure of LPG in MSV
Head loss to be calculated based on rated pump discharge & based on proper selection of low velosity & pipe diameter combination.
Calculation of pump head (operating condition) | Act head required at filling gun + actual static head discharge side +Head loss with instant Q - Act Static head suction side - Act vapor pressure of LPG at given tempr
Chezy's formula |  |  | Page 466 RK Bansal | Head loss by Chezy's formula usualy larger than Darcy's
Chezy's f' = Density * darcy's friction co-efficent / 2 |  | Article 10.3.1 in RK bansal pg 436
Chezy's Consstant | C | 99.0454 | Usualy it is given independent of darcy's co-ficient.
Area / Perimeter Ration for pipe | m | 0.0375
Head loss per meter | i=h/L | 0.0016792
Net Head loss | h | 0.50375 | Check Darcy's also
After Pump is purchased
Rated Flow |  | 0.013889 | 0.11785 | 50 | This for design Head vs Design flow only, for actual head vs flow you need to refer pump perfromance curve
Rated Head |  | 162 | 45.4084 |  | In design H vs Q graph, Q increases with increase in H (this can be called pumps graph), Q can be obtained by specifics speed method
Rated Speed |  | 2970 |  |  | When pump is connected to real load, Q decreases with increase in load(H), Q can be obtained by performance curve ( perfornce curve can be called load's H vs Q graph)
Efficiency |  | 52% |  |  | Don’t confuse design curve with load curve
Specific Speed |  | 7.7082 |  |  | Head of pump is irrespective of liquid - It is work done on per unit weight of liquid per second.
Actual Head of connected piping |  | 140 | 40.7002 |  | 162m head pump will generate same head for water, petrol diesle or LPG but pressure generated will be different based on density
Actual flow |  | 0.011158 | 0.10563 | 40.1689 | Head is irrespective of media, Prove it
Diameter of pipe
Velosity
Dynamic Viscosity
Kinamatic Viscosity
Note on F7: Author: Blausius Eqn

## DataSheet
Dynamic Viscosity of Propane | 0.00011 | N-S/M2 | Engineeringtoolbox.com
Kinematic Viscosity of LPG | 4e-07 | M2/s | LPG Pup Data sheet KEPL | one stoke = 10 ^ -4 M2/s, one Cstockes = 10^-6M2/s
0.000218

## TSV
| Kg | Pascal
Pressure | 21 | 2100000
Density | 545
g | 9.81
Head | 392.784
Exit Velo | 87.7862
Dia | 0.025
Area | 0.00049087 |  | 206.167 | 21.016
Q | 0.043092
m | 23.4851 |  |  |  | 2.7383 | 240.3833 | 24.5039 | 73.5117 | 6.2e-06
N | 2061.6702 | [6 empty] | 11856726.6154 | 11.8567
Do | 0.0342 | 1.3681e-06
Di | 0.0333 | 1.2296e-06